## Default
Internal id | Base | Template | Name | Display Name | Tags | Relations | Address |  |  | Alarm |  |  |  |  | History |  |  |  |  | Facets
Id to reuse the component. Use # | Reference where the component will be created | Template name(include subpath if needed) | Name of the instance to create | Display Name of the instance to create | Define the tag key in the column header or in the cells separated with ; | Define relations id and the endpoint | See Help sheet to get the syntaxes |  |  | Create/Update an alarm extension |  |  |  |  | Create/Update a history extension |  |  |  |  | Set the facets for the component
[5 empty] | markers |  | address1 | address2 | address3 | model | name | alarmClass | lowLimit | highLimit | model | name | interval | changeTolerance | capacity
#Modbus | $Drivers | $ModbusAsyncNetwork | Modbus
#Meter1 | #Modbus | $ModbusAsyncDevice | Meter1
#Meter2 | #Modbus | $ModbusAsyncDevice | Meter2
Note on A4: Christophe HOLC: The internal id is a value that won't have any consequence in your station. Inside the Excel file, you can reuse it as a shortcut. In this file, we use it in the B5 and B6 cells
Note on C4: Christophe HOLC: Here the templates use a variable. Go to the ~Variables Sheet to see which values are associated to those variables
Note on B5: Christophe HOLC: The base indicates the parent of the component in this row. Here it's the id used in the first line, so this component will be created in the component defined in the first line, the ModbusAsyncNetwork named Modbus

## ~Structure
Sheet name | Predicate
Default | n:network or n:device or n:childPoint<-n:device

## ~Address Help
Help on equipment and point address
NETWORKS ADDRESS | Network | Address 1 | Format | Address 2 | Format
| ModbusTcpGateway | IP Address | nnn.nnn.nnn.nnn | Port | nnnnn
| SysmikScaIoNetwork | IP Address | nnn.nnn.nnn.nnn | Port | nnnnn
EQUIPEMENTS ADDRESS | Network | Address 1 | Format | Address 2 | Format | Address 3 | Format
| BACnet | Network Number | nnn | Device ID | nnnnn | Mac address | "suffix:value" or a value in hexadecimal (hh hh hh hh hh) suffix: unknown/ethernet/ip/mstp value: heaxadecimals or ip according to the suffix (must have the same format as in the MAC Address slot)
| Eibnet | IP Adress | nnn.nnn.nnn.nnn | Mac address
| KnxnetIpNetwork | IP Address | nnn.nnn.nnn.nnn | Control Port Number ¦ Individual Device Address | n¦n.n.n
| Lonworks | NeuronId | hh hh hh hh hh hh | Subnet Node Id | subnet/node
| Mbus | Primary Adress | nnnnnnnn | Secondary Adress | nnnnnnnn | Ident Number | String value of the Ident Number
| Modbus TCP | Slave Address | n | IP Address | nnn.nnn.nnn.nnn
| Modbus RS485 | Slave Address | n
| NiagaraStation | Adress | Ord (example: ip:nnn.nnn.nnn.nnn) | Port | nnnn | scheme | fox/foxs
| Nrio | Address | nn | Device Type | "none" or "baseBoardReader" or "remoteReader" or "remoteInputOutput" or "io16"
| Opc | Address Hex | nnnnnnnnnnnn
| Snmp/nSnmp | IP Adress | nnn.nnn.nnn.nnn | Port | nnnn
| Sysmik | Terminal | nnn
POINTS ADDRESS | Network | Address 1 | Format | Address 2 | Format | Address 3 | Format
| BBacnetProxyExt | objectId Type | objectType | objectId | instanceNumber | propertyId | The BACnet property name proxied by the point. "presentValue"/"Event State" ... depending on selection
| EibNetwork BKnxProxyExt | groupAddresses | n/n/n;n/n/n separated by ; . A list of group addresses from which the value of this proxy extension can be updated. The first group address in the list is the primary group address and cannot be deleted, but can be edited. The primary group address is the address to which any read or write request will be directed from this proxy extension. | dataType | 1-14 byte in the left hand pull down, with each appropriate data type that matches that data size contained in the right-hand pull down.
| KNX driver: BKnxNumericProxyExt BKnxBooleanProxyExt BKnxEnumProxyExt BKnxStringProxyExt | groupAddresses | n/n/n n/n/n... separated by a space . A list of group addresses from which the value of this proxy extension can be updated. The first group address in the list is the primary group address and cannot be deleted, but can be edited. The primary group address is the address to which any read or write request will be directed from this proxy extension. | dataValueTypeID | Value id only like "DPST-1-1". The number of bits and the description should not be indicated
| LonProxy | targetComp | Pathname for target BLonData relative to device | targetName | Name of BLonPrimitive this proxy targets
| BModbusClientBooleanProxyExt | dataAddress | "suffix:value" suffix: dec/hex/modbus value:integer or string according to the suffix
| BModbusClientEnumBitsProxyExt | dataAddress | "suffix:value" suffix: dec/hex/modbus value:integer or string according to the suffix | beginningBit | first bits 0 to 15 | numberOfBits | Number of bits read in the register. Starting with the "beginningBit"
| BModbusClientNumericBitsProxyExt | dataAddress | "suffix:value" suffix: dec/hex/modbus value:integer or string according to the suffix | beginningBit | first bits 0 to 15 | numberOfBits | Number of bits read in the register. Starting with the "beginningBit"
| BModbusClientNumericProxyExt | dataAddress | "suffix:value" suffix: dec/hex/modbus value:integer or string according to the suffix
| BModbusClientRegisterBitProxyExt | dataAddress | "suffix:value" suffix: dec/hex/modbus value:integer or string according to the suffix | bitNumber | n
| BNiagaraproxyExt | pointId | String value of the point ID
| BNrioProxyExt | instance | integer value of the instance number
| BModbusClientStringProxyExt | dataAddress | "suffix:value" suffix: dec/hex/modbus value:integer or string according to the suffix | numberRegisters | Number of consecutive holding registers to read, starting with the specified Absolute Address. (Example : 4A41 hex)
| BOpcProxyExt | id | Unique ID of the data item on the server, | opcDataType | Vt Type (example : Vt Real, Vt Uint2, Vt Boolean…)
| BSnmpProxyExt/BSnmpObjectExt/BNSnmpProxyExt | objectIdentifier | index value that corresponds to the column index of the object created for it in the Tridium Input or Output Table. | variableType | This property specifies the value type that is written out to the SNMP device at the location of the OID specified in the Object Identifier property
| Sysmik AiEcoT | channel | nnn | tempType | EcoTInputEnum tag (celsius, fahrenheit)
| Sysmik AiT | channel | nnn | aiType | TInputEnum tag (resistance_400Ohm, resistance_4kOhm, temperature_Ni1000…) | wireType | WireTypeEnum tag (wire_2, wire_2, wire_4)
| Sysmik AiU | channel | nnn | aiType | UInputEnum tag (auto, voltage_0_10V, resistance_3kOhm, resistance_30kOhm…)
| Sysmik AiVA | channel | nnn | aiType | VAInputEnum tag (auto, voltage_0_10_V, current_0_20_mA)
| Sysmik (others) | channel | nnn

## ~Variables
General |  | Alarms |  | Histories |  | Conversions |  | Facets
Artifact | Value | Artifact | Value | Artifact | Value | Artifact | Value | Artifact | Value
$ModbusAsyncNetwork | modbusAsync:ModbusAsyncNetwork | $OutOfRange | excel:OutOfRangeAlarmExt | $NumericInterval | history:NumericIntervalHistoryExt | $NO | Default | $BooleanFacet | trueText=s:true;falseText=s:false
$ModbusAsyncDevice | modbusAsync:ModbusAsyncDevice | $StringChangeOfValue | excel:StringChangeOfValueAlarmExt | $NumericCov | history:NumericCovHistoryExt | $NF | ReversePolarity | $EnumFacet | range={}
$Station | slot: | $BooleanChangeOfState | excel:BooleanChangeOfStateAlarmExt | $BooleanInterval | history:BooleanIntervalHistoryExt | $Linear | Linear(1,1) | $NumericFacet | min=-inf;max=+inf;precision=i:1;units=null
$Drivers | slot:/Drivers | $BooleanCommandFailure | excel:BooleanCommandFailureAlarmExt | $BooleanCov | history:BooleanCovHistoryExt
$Num | control:NumericPoint | $EnumChangeOfState | excel:EnumChangeOfStateAlarmExt | $EnumInterval | history:EnumIntervalHistoryExt
$Bool | control:BooleanPoint | $EnumCommandFailure | excel:EnumCommandFailureAlarmExt | $EnumCov | history:EnumCovHistoryExt
$Enum | control:EnumPoint | $Status | excel:StatusAlarmExt | $StringInterval | history:StringIntervalHistoryExt
$String | control:StringPoint | $Loop | excel:LoopAlarmExt | $StringCov | history:StringCovHistoryExt
$BooleanSchedule | schedule:BooleanSchedule | $ElapsedActiveTime | excel:ElapsedActiveTimeAlarmExt
|  | $ChangeOfStateCount | excel:ChangeOfStateCountAlarmExt