## Default
Internal id | Base | Template | Name | Display Name | History
Id to reuse the component. Use # | Reference where the component will be created | Template name(include subpath if needed) | Name of the instance to create | Display Name of the instance to create
[5 empty] | model | name | slot:enabled
#BacnetNetwork | $Drivers | bacnet:BacnetNetwork | BacnetNetwork
#AHU_01 | #BacnetNetwork | bacnet:BacnetDevice | AHU_01
| #AHU_01/points | $Bool | BooleanPoint |  | history:BooleanIntervalHistoryExt | BooleanInt | true

## ~Structure
Sheet name | Predicate
Default | n:network or n:device or n:childPoint<-n:device

## ~Help
Help on equipment and point address
NETWORKS ADDRESS | Network | Address 1 | Format | Address 2 | Format
| ModbusTcpGateway | IP Address | nnn.nnn.nnn.nnn | Port | nnnnn
| SysmikScaIoNetwork | IP Address | nnn.nnn.nnn.nnn | Port | nnnnn
EQUIPEMENTS ADDRESS | Network | Address 1 | Format | Address 2 | Format | Address 3 | Format
| BACnet | Network Number | nnn | Instance Number | nnnnn | Mac address | hh…
| Eibnet | IP Adress | nnn.nnn.nnn.nnn | Mac address
| KnxnetIpNetwork | IP Address | nnn.nnn.nnn.nnn | Control Port Number ¦ Individual Device Address | n¦n.n.n
| Lonworks | NeuronId | hh hh hh hh hh hh | Subnet Node Id | subnet/node
| Mbus | Primary Adress | nnnnnnnn | Secondary Adress | nnnnnnnn
| Modbus TCP | Slave Address | n | IP Address | nnn.nnn.nnn.nnn
| Modbus RS485 | Slave Address | n | Port | nnnn | scheme | fox/foxs
| NiagaraStation | Adress | Ord (example: ip:nnn.nnn.nnn.nnn)
| Nrio | Address | nn | Device Type | "none" or "baseBoardReader" or "remoteReader" or "remoteInputOutput" or "io16"
| Opc | Address Hex | nnnnnnnnnnnn
| Snmp/nSnmp | IP Adress | nnn.nnn.nnn.nnn | Port | nnnn
| Sysmik | Terminal | nnn
POINTS ADDRESS | Network | Address 1 | Format | Address 2 | Format | Address 3 | Format
| BBacnetProxyExt | objectId Type | objectType | objectId | instanceNumber | propertyId | The BACnet property name proxied by the point. "presentValue"/"Event State" ... depending on selection
| EibNetwork BKnxProxyExt | groupAddresses | n/n/n;n/n/n separated by ; . A list of group addresses from which the value of this proxy extension can be updated. The first group address in the list is the primary group address and cannot be deleted, but can be edited. The primary group address is the address to which any read or write request will be directed from this proxy extension. | dataType | 1-14 byte in the left hand pull down, with each appropriate data type that matches that data size contained in the right-hand pull down.
| KNX driver: BKnxNumericProxyExt BKnxBooleanProxyExt BKnxEnumProxyExt BKnxStringProxyExt | groupAddresses | n/n/n n/n/n... separated by a space . A list of group addresses from which the value of this proxy extension can be updated. The first group address in the list is the primary group address and cannot be deleted, but can be edited. The primary group address is the address to which any read or write request will be directed from this proxy extension. | dataValueTypeID | Value id only like "DPST-1-1". The number of bits and the description should not be indicated
| LonProxy | targetComp | Pathname for target BLonData relative to device | targetName | Name of BLonPrimitive this proxy targets
| BModbusClientBooleanProxyExt | dataAddress | "suffix:value" suffix: decimal/hex/modbus value:integer or string according to the suffix
| BModbusClientEnumBitsProxyExt | dataAddress | "suffix:value" suffix: decimal/hex/modbus value:integer or string according to the suffix | beginningBit | first bits 0 to 15 | numberOfBits | Number of bits read in the register. Starting with the "beginningBit"
| BModbusClientNumericBitsProxyExt | dataAddress | "suffix:value" suffix: decimal/hex/modbus value:integer or string according to the suffix | beginningBit | first bits 0 to 15 | numberOfBits | Number of bits read in the register. Starting with the "beginningBit"
| BModbusClientNumericProxyExt | dataAddress | "suffix:value" suffix: decimal/hex/modbus value:integer or string according to the suffix
| BModbusClientRegisterBitProxyExt | dataAddress | "suffix:value" suffix: decimal/hex/modbus value:integer or string according to the suffix | bitNumber | n
| BNiagaraproxyExt | pointId | String value of the point ID
| BNrioProxyExt | instance | integer value of the instance number
| BModbusClientStringProxyExt | dataAddress | "suffix:value" suffix: decimal/hex/modbus value:integer or string according to the suffix | numberRegisters | Number of consecutive holding registers to read, starting with the specified Absolute Address. (Example : 4A41 hex)
| BOpcProxyExt | id | Unique ID of the data item on the server, | opcDataType | Vt Type (example : Vt Real, Vt Uint2, Vt Boolean…)
| BSnmpProxyExt/BSnmpObjectExt/BNSnmpProxyExt | objectIdentifier | index value that corresponds to the column index of the object created for it in the Tridium Input or Output Table. | variableType | This property specifies the value type that is written out to the SNMP device at the location of the OID specified in the Object Identifier property
| Sysmik AiEcoT | channel | nnn | tempType | EcoTInputEnum tag (celsius, fahrenheit)
| Sysmik AiT | channel | nnn | aiType | TInputEnum tag (resistance_400Ohm, resistance_4kOhm, temperature_Ni1000…) | wireType | WireTypeEnum tag (wire_2, wire_2, wire_4)
| Sysmik AiU | channel | nnn | aiType | UInputEnum tag (auto, voltage_0_10V, resistance_3kOhm, resistance_30kOhm…)
| Sysmik AiVA | channel | nnn | aiType | VAInputEnum tag (auto, voltage_0_10_V, current_0_20_mA)
| Sysmik (others) | channel | nnn

## ~Model
Equipment | Location | Nature | Subsystem
I*/*O Module | Building1 | 3 Way | HVAC
I*/*O Module/ISMA-4I4O-H | Building1/Level1 | AHU Ductwork | Plumbing
I*/*O Module/ISMA-4I4O-H-IP | Le Rabelais | AHU Ductwork/Dual Duct
I*/*O Module/ISMA-4O-H | Le Rabelais/Ground floor | AHU Ductwork/Single Duct
I*/*O Module/ISMA-4O-H-IP | Le Rabelais/Level 1 | AHU Ductwork/Triple Duct
I*/*O Module/ISMA-4TO-H | Le Rabelais/Roof floor | AHU Flow Type
I*/*O Module/ISMA-4TO-H-IP |  | AHU Flow Type/Constant Volume
I*/*O Module/ISMA-4U4A-H |  | AHU Flow Type/Variable Volume
I*/*O Module/ISMA-4U4A-H-IP |  | AHU Zone Delivery
I*/*O Module/ISMA-4U4O-H |  | AHU Zone Delivery/Chilled Beam Zone
I*/*O Module/ISMA-4U4O-H-IP |  | AHU Zone Delivery/Direct Zone
I*/*O Module/ISMA-8I-H |  | AHU Zone Delivery/Multi Zone
I*/*O Module/ISMA-8I-H-IP |  | AHU Zone Delivery/VAV Zone
I*/*O Module/ISMA-8U-H |  | Access
I*/*O Module/ISMA-8U-H-IP |  | Air
I*/*O Module/ISMA-MIX18 |  | Air Handling
I*/*O Module/ISMA-MIX18-IP |  | Air Handling/AHU
I*/*O Module/ISMA-MIX38 |  | Air Handling/AHU/Acknowledgment
I*/*O Module/ISMA-MIX38-IP |  | Air Handling/AHU/Air Humidity Setpoint
Network Element |  | Air Handling/AHU/Air Pressure Setpoint
Network Element/ISMA-MG-IP |  | Air Handling/AHU/Air Temperature Effective Setpoint
Networked Actuators |  | Air Handling/AHU/Air Temperature Setpoint
Networked Meters |  | Air Handling/AHU/Alarm Synthesis
Networked Sensors |  | Air Handling/AHU/Boolean Default
Preloaded Application Controller |  | Air Handling/AHU/Building Static Pressure
Preloaded Application Controller/EXCEL10 |  | Air Handling/AHU/Building Static Pressure Setpoint
Preloaded Application Controller/ISMA-2D |  | Air Handling/AHU/Changeover Coil
Preloaded Application Controller/ISMA-2D-WD |  | Air Handling/AHU/Chilled Water Pump Command
Preloaded Application Controller/ISMA-2D1B |  | Air Handling/AHU/Chilled Water Pump Status
Preloaded Application Controller/ISMA-2D1B-WD |  | Air Handling/AHU/Cooling Coil
Preloaded Application Controller/ISMA-FCU-HH |  | Air Handling/AHU/Cooling Coil/Chilled Water Flow
Preloaded Application Controller/ISMA-FCU-HL |  | Air Handling/AHU/Cooling Coil/Chilled Water Pump Command
Preloaded Application Controller/ISMA-FCU-LL |  | Air Handling/AHU/Cooling Coil/Chilled Water Pump Status
Programmable Logic Controller |  | Air Handling/AHU/Cooling Coil/Chilled Water Temp Entering
Programmable Logic Controller/ISMA-AAC20 |  | Air Handling/AHU/Cooling Coil/Chilled Water Temp Leaving
Programmable Logic Controller/ISMA-AAC20-D |  | Air Handling/AHU/Cooling Coil/Chilled Water Valve Command
Programmable Logic Controller/ISMA-AAC20-LCD |  | Air Handling/AHU/Cooling Coil/Chilled Water Valve Position
Programmable Logic Controller/ISMA-AAC20-LCD-D |  | Air Handling/AHU/Cooling Coil/Cool Stage Command
Programmable Logic Controller/ISMA-AAC20-LCD-M |  | Air Handling/AHU/Cooling Coil/Cooling Coil Air Leaving Humidity
Programmable Logic Controller/ISMA-AAC20-M |  | Air Handling/AHU/Cooling Coil/Cooling Coil Air Leaving Temp
Server |  | Air Handling/AHU/Cooling Coil/Pipe Temperature Sensor
Air Handling/AHU/Cooling Coil/Pump
Air Handling/AHU/Cooling Coil/Pump Boolean Command
Air Handling/AHU/Cooling Coil/Pump/Boolean Default
Air Handling/AHU/Cooling Coil/Running State
Air Handling/AHU/Damper
Air Handling/AHU/Damper/Boolean Default
Air Handling/AHU/Damper/Damper Analog Command
Air Handling/AHU/Damper/Damper Boolean Command
Air Handling/AHU/Damper/Damper Position
Air Handling/AHU/Damper/Damper State
Air Handling/AHU/Damper/Mixed Air Damper Analog Command
Air Handling/AHU/Damper/Outside Air Damper Analog Command
Air Handling/AHU/Damper/Outside Air Damper Boolean Command
Air Handling/AHU/Damper/Return Air Damper Analog Command
Air Handling/AHU/Dehumidifier
Air Handling/AHU/Dehumidifier/Boolean Default
Air Handling/AHU/Dehumidifier/DeHumidify Mode
Air Handling/AHU/Dehumidifier/Duct Temperature Sensor
Air Handling/AHU/Discharge Air Flow Setpoint Effective
Air Handling/AHU/Duct
Air Handling/AHU/Duct/Boolean Default
Air Handling/AHU/Duct/Discharge Air Flow
Air Handling/AHU/Duct/Discharge Air Humidity
Air Handling/AHU/Duct/Discharge Air Pressure
Air Handling/AHU/Duct/Discharge Air Pressure Setpoint
Air Handling/AHU/Duct/Discharge Air Temperature
Air Handling/AHU/Duct/Discharge Air Temperature Setpoint
Air Handling/AHU/Duct/Duct CO2 Sensor
Air Handling/AHU/Duct/Duct Flow Control
Air Handling/AHU/Duct/Duct Humidity Sensor
Air Handling/AHU/Duct/Duct Pressure Sensor
Air Handling/AHU/Duct/Duct Temperature Sensor
Air Handling/AHU/Duct/Flow Sensor
Air Handling/AHU/Duct/Mixed Air Temperature
Air Handling/AHU/Duct/Outside Air Flow
Air Handling/AHU/Duct/Outside Air Humidity
Air Handling/AHU/Duct/Outside Air Temperature
Air Handling/AHU/Duct/Return Air CO2
Air Handling/AHU/Duct/Return Air DeHumidify Setpoint
Air Handling/AHU/Duct/Return Air Humidify Setpoint
Air Handling/AHU/Duct/Return Air Humidity
Air Handling/AHU/Duct/Return Air Pressure
Air Handling/AHU/Duct/Return Air Pressure Setpoint
Air Handling/AHU/Duct/Return Air Temperature
Air Handling/AHU/Duct/Return CO2 Setpoint
Air Handling/AHU/Economize Mode
Air Handling/AHU/Effective Command
Air Handling/AHU/Electric Heating Coil
Air Handling/AHU/Electrical Cabinet
Air Handling/AHU/Electrical Cabinet/Switch State
Air Handling/AHU/Fan
Air Handling/AHU/Fan/Boolean Default
Air Handling/AHU/Fan/Boolean Fan Command
Air Handling/AHU/Fan/Discharge Air Fan Frequency
Air Handling/AHU/Fan/Discharge Air Fan Speed
Air Handling/AHU/Fan/Discharge Air Fan Status
Air Handling/AHU/Fan/Discharge Fan Command
Air Handling/AHU/Fan/Duct Flow Control
Air Handling/AHU/Fan/Elapsed Active Time
Air Handling/AHU/Fan/Electrical Current
Air Handling/AHU/Fan/Electrical Energy Consumption
Air Handling/AHU/Fan/Fan Speed Setpoint
Air Handling/AHU/Fan/Flow Sensor
Air Handling/AHU/Fan/Multi Speed Fan Command
Air Handling/AHU/Fan/Multi Speed Fan State
Air Handling/AHU/Fan/Return Air Fan Command
Air Handling/AHU/Fan/Return Air Fan Frequency
Air Handling/AHU/Fan/Return Air Fan Speed
Air Handling/AHU/Fan/Return Air Fan Status
Air Handling/AHU/Fan/Running State
Air Handling/AHU/Fan/Variable Fan Command
Air Handling/AHU/Fan/Variable Fan State
Air Handling/AHU/Filter
Air Handling/AHU/Filter/Filter Alarm
Air Handling/AHU/Filter/Filter Pressure Delta
Air Handling/AHU/HVAC Mode Command
Air Handling/AHU/Heat Exchanger
Air Handling/AHU/Heat Exchanger/Boolean Default
Air Handling/AHU/Heat Recovery Coil
Air Handling/AHU/Heat Recovery Coil/Heat Recovery Air Leaving Temp
Air Handling/AHU/Heat Recovery Coil/Heat Recovery Pump Command
Air Handling/AHU/Heat Recovery Coil/Heat Recovery Water Energy
Air Handling/AHU/Heat Recovery Coil/Heat Recovery Water Power
Air Handling/AHU/Heat Recovery Coil/Heat Recovery Water Temp Entering
Air Handling/AHU/Heat Recovery Coil/Heat Recovery Water Temp Leaving
Air Handling/AHU/Heat Recovery Coil/Heat Recovery Water Volumetric Flow
Air Handling/AHU/Heat Wheel
Air Handling/AHU/Heat Wheel/Boolean Default
Air Handling/AHU/Heat Wheel/Heat Wheel Command
Air Handling/AHU/Heat Wheel/Heat Wheel Speed Command
Air Handling/AHU/Heat Wheel/Heat Wheel State
Air Handling/AHU/Heating Coil
Air Handling/AHU/Heating Coil/Heat Stage Command
Air Handling/AHU/Heating Coil/Heating Coil Air Leaving Temp
Air Handling/AHU/Heating Coil/Hot Water Circulation Pump Command
Air Handling/AHU/Heating Coil/Hot Water Circulation Pump Status
Air Handling/AHU/Heating Coil/Hot Water Flow
Air Handling/AHU/Heating Coil/Hot Water Temp Entering
Air Handling/AHU/Heating Coil/Hot Water Temp Leaving
Air Handling/AHU/Heating Coil/Hot Water Valve Command
Air Handling/AHU/Heating Coil/Hot Water Valve Status
Air Handling/AHU/Heating Coil/Pipe Temperature Sensor
Air Handling/AHU/Heating Coil/Pump
Air Handling/AHU/Heating Coil/Pump Boolean Command
Air Handling/AHU/Heating Coil/Pump/Boolean Default
Air Handling/AHU/Heating Coil/Running State
Air Handling/AHU/Hot Water Circulation Pump Command
Air Handling/AHU/Hot Water Circulation Pump Status
Air Handling/AHU/Humidifier
Air Handling/AHU/Humidifier/Analog Humidifier Command
Air Handling/AHU/Humidifier/Boolean Default
Air Handling/AHU/Humidifier/Boolean Humidifier Command
Air Handling/AHU/Humidifier/High Level Humidifier Alarm
Air Handling/AHU/Humidifier/Humidifier Dry Level Alarm
Air Handling/AHU/Humidifier/Humidifier Enable
Air Handling/AHU/Humidifier/Humidifier Overrun Alarm
Air Handling/AHU/Humidifier/Humidifier Pump Speed Command
Air Handling/AHU/Humidifier/Humidifier Valve Command
Air Handling/AHU/Humidifier/Humidifier Valve Position
Air Handling/AHU/Humidifier/Humidifier Water Disinfection State
Air Handling/AHU/Humidifier/Low Level Humidifier Alarm
Air Handling/AHU/Humidifier/Pump
Air Handling/AHU/Humidifier/Pump Boolean Command
Air Handling/AHU/Humidifier/Pump/Boolean Default
Air Handling/AHU/Humidifier/Running State
Air Handling/AHU/Humidifier/Water Disinfection System
Air Handling/AHU/Humidifier/Water Disinfection System/Boolean Default
Air Handling/AHU/Information
Air Handling/AHU/Mode Command
Air Handling/AHU/Occupied Cooling Setpoint
Air Handling/AHU/Occupied Heating Setpoint
Air Handling/AHU/Occupied Mode
Air Handling/AHU/Pre Heating Coil
Air Handling/AHU/Pre Heating Coil/Hot Water Circulation Pump Command
Air Handling/AHU/Pre Heating Coil/Hot Water Circulation Pump Status
Air Handling/AHU/Pre Heating Coil/Hot Water Flow
Air Handling/AHU/Pre Heating Coil/Hot Water Temp Entering
Air Handling/AHU/Pre Heating Coil/Hot Water Temp Leaving
Air Handling/AHU/Pre Heating Coil/Pipe Temperature Sensor
Air Handling/AHU/Pre Heating Coil/PreHeat Coil Air Leaving Temp
Air Handling/AHU/Pre Heating Coil/Preheat Valve Command
Air Handling/AHU/Pre Heating Coil/Preheat Valve Status
Air Handling/AHU/Pre Heating Coil/Pump
Air Handling/AHU/Pre Heating Coil/Pump Boolean Command
Air Handling/AHU/Pre Heating Coil/Pump/Boolean Default
Air Handling/AHU/Pre Heating Coil/Running State
Air Handling/AHU/Running Command
Air Handling/AHU/Running Priority
Air Handling/AHU/Running State
Air Handling/AHU/Setting
Air Handling/AHU/Unoccupied Cooling Setpoint
Air Handling/AHU/Unoccupied Heating Setpoint
Air Handling/AHU/Zone Air Quality Sensor
Air Handling/AHU/Zone CO Sensor
Air Handling/AHU/Zone CO2
Air Handling/AHU/Zone CO2 Setpoint
Air Handling/AHU/Zone Humidity
Air Handling/AHU/Zone Pressure
Air Handling/AHU/Zone Pressure Setpoint
Air Handling/AHU/Zone Temperature
Air Handling/AHU/Zone Temperature Setpoint Effective
Air Handling/CRAC
Air Handling/CRAC/Air Temperature Setpoint
Air Handling/CRAC/Alarm Synthesis
Air Handling/CRAC/Cooling Coil
Air Handling/CRAC/Cooling Coil/Chilled Water Flow
Air Handling/CRAC/Cooling Coil/Chilled Water Pump Command
Air Handling/CRAC/Cooling Coil/Chilled Water Pump Status
Air Handling/CRAC/Cooling Coil/Chilled Water Temp Entering
Air Handling/CRAC/Cooling Coil/Chilled Water Temp Leaving
Air Handling/CRAC/Cooling Coil/Chilled Water Valve Command
Air Handling/CRAC/Cooling Coil/Chilled Water Valve Position
Air Handling/CRAC/Cooling Coil/Cool Stage Command
Air Handling/CRAC/Cooling Coil/Cooling Coil Air Leaving Humidity
Air Handling/CRAC/Cooling Coil/Cooling Coil Air Leaving Temp
Air Handling/CRAC/Cooling Coil/Pipe Temperature Sensor
Air Handling/CRAC/Cooling Coil/Pump
Air Handling/CRAC/Cooling Coil/Pump Boolean Command
Air Handling/CRAC/Cooling Coil/Pump/Boolean Default
Air Handling/CRAC/Cooling Coil/Running State
Air Handling/CRAC/Fan
Air Handling/CRAC/Fan/Boolean Default
Air Handling/CRAC/Fan/Boolean Fan Command
Air Handling/CRAC/Fan/Discharge Air Fan Frequency
Air Handling/CRAC/Fan/Discharge Air Fan Speed
Air Handling/CRAC/Fan/Discharge Air Fan Status
Air Handling/CRAC/Fan/Discharge Fan Command
Air Handling/CRAC/Fan/Duct Flow Control
Air Handling/CRAC/Fan/Elapsed Active Time
Air Handling/CRAC/Fan/Electrical Current
Air Handling/CRAC/Fan/Electrical Energy Consumption
Air Handling/CRAC/Fan/Fan Speed Setpoint
Air Handling/CRAC/Fan/Flow Sensor
Air Handling/CRAC/Fan/Multi Speed Fan Command
Air Handling/CRAC/Fan/Multi Speed Fan State
Air Handling/CRAC/Fan/Return Air Fan Command
Air Handling/CRAC/Fan/Return Air Fan Frequency
Air Handling/CRAC/Fan/Return Air Fan Speed
Air Handling/CRAC/Fan/Return Air Fan Status
Air Handling/CRAC/Fan/Running State
Air Handling/CRAC/Fan/Variable Fan Command
Air Handling/CRAC/Fan/Variable Fan State
Air Handling/CRAC/Humidifier
Air Handling/CRAC/Humidifier/Analog Humidifier Command
Air Handling/CRAC/Humidifier/Boolean Default
Air Handling/CRAC/Humidifier/Boolean Humidifier Command
Air Handling/CRAC/Humidifier/High Level Humidifier Alarm
Air Handling/CRAC/Humidifier/Humidifier Dry Level Alarm
Air Handling/CRAC/Humidifier/Humidifier Enable
Air Handling/CRAC/Humidifier/Humidifier Overrun Alarm
Air Handling/CRAC/Humidifier/Humidifier Pump Speed Command
Air Handling/CRAC/Humidifier/Humidifier Valve Command
Air Handling/CRAC/Humidifier/Humidifier Valve Position
Air Handling/CRAC/Humidifier/Humidifier Water Disinfection State
Air Handling/CRAC/Humidifier/Low Level Humidifier Alarm
Air Handling/CRAC/Humidifier/Pump
Air Handling/CRAC/Humidifier/Pump Boolean Command
Air Handling/CRAC/Humidifier/Pump/Boolean Default
Air Handling/CRAC/Humidifier/Running State
Air Handling/CRAC/Humidifier/Water Disinfection System
Air Handling/CRAC/Humidifier/Water Disinfection System/Boolean Default
Air Handling/CRAC/Zone Humidity
Air Handling/CRAC/Zone Temperature
Air Handling/Discharge Fan
Air Handling/Discharge Fan/Fan
Air Handling/Discharge Fan/Fan/Boolean Default
Air Handling/Discharge Fan/Fan/Boolean Fan Command
Air Handling/Discharge Fan/Fan/Discharge Air Fan Frequency
Air Handling/Discharge Fan/Fan/Discharge Air Fan Speed
Air Handling/Discharge Fan/Fan/Discharge Air Fan Status
Air Handling/Discharge Fan/Fan/Discharge Fan Command
Air Handling/Discharge Fan/Fan/Duct Flow Control
Air Handling/Discharge Fan/Fan/Elapsed Active Time
Air Handling/Discharge Fan/Fan/Electrical Current
Air Handling/Discharge Fan/Fan/Electrical Energy Consumption
Air Handling/Discharge Fan/Fan/Fan Speed Setpoint
Air Handling/Discharge Fan/Fan/Flow Sensor
Air Handling/Discharge Fan/Fan/Multi Speed Fan Command
Air Handling/Discharge Fan/Fan/Multi Speed Fan State
Air Handling/Discharge Fan/Fan/Return Air Fan Command
Air Handling/Discharge Fan/Fan/Return Air Fan Frequency
Air Handling/Discharge Fan/Fan/Return Air Fan Speed
Air Handling/Discharge Fan/Fan/Return Air Fan Status
Air Handling/Discharge Fan/Fan/Running State
Air Handling/Discharge Fan/Fan/Variable Fan Command
Air Handling/Discharge Fan/Fan/Variable Fan State
Air Handling/Exhaust Fan
Air Handling/Exhaust Fan/CMV
Air Handling/Exhaust Fan/CMV/Fan
Air Handling/Exhaust Fan/CMV/Fan/Boolean Default
Air Handling/Exhaust Fan/CMV/Fan/Boolean Fan Command
Air Handling/Exhaust Fan/CMV/Fan/Discharge Air Fan Frequency
Air Handling/Exhaust Fan/CMV/Fan/Discharge Air Fan Speed
Air Handling/Exhaust Fan/CMV/Fan/Discharge Air Fan Status
Air Handling/Exhaust Fan/CMV/Fan/Discharge Fan Command
Air Handling/Exhaust Fan/CMV/Fan/Duct Flow Control
Air Handling/Exhaust Fan/CMV/Fan/Elapsed Active Time
Air Handling/Exhaust Fan/CMV/Fan/Electrical Current
Air Handling/Exhaust Fan/CMV/Fan/Electrical Energy Consumption
Air Handling/Exhaust Fan/CMV/Fan/Fan Speed Setpoint
Air Handling/Exhaust Fan/CMV/Fan/Flow Sensor
Air Handling/Exhaust Fan/CMV/Fan/Multi Speed Fan Command
Air Handling/Exhaust Fan/CMV/Fan/Multi Speed Fan State
Air Handling/Exhaust Fan/CMV/Fan/Return Air Fan Command
Air Handling/Exhaust Fan/CMV/Fan/Return Air Fan Frequency
Air Handling/Exhaust Fan/CMV/Fan/Return Air Fan Speed
Air Handling/Exhaust Fan/CMV/Fan/Return Air Fan Status
Air Handling/Exhaust Fan/CMV/Fan/Running State
Air Handling/Exhaust Fan/CMV/Fan/Variable Fan Command
Air Handling/Exhaust Fan/CMV/Fan/Variable Fan State
Air Handling/Exhaust Fan/Damper
Air Handling/Exhaust Fan/Damper/Boolean Default
Air Handling/Exhaust Fan/Damper/Damper Analog Command
Air Handling/Exhaust Fan/Damper/Damper Boolean Command
Air Handling/Exhaust Fan/Damper/Damper Position
Air Handling/Exhaust Fan/Damper/Damper State
Air Handling/Exhaust Fan/Damper/Mixed Air Damper Analog Command
Air Handling/Exhaust Fan/Damper/Outside Air Damper Analog Command
Air Handling/Exhaust Fan/Damper/Outside Air Damper Boolean Command
Air Handling/Exhaust Fan/Damper/Return Air Damper Analog Command
Air Handling/Exhaust Fan/Duct
Air Handling/Exhaust Fan/Duct/Boolean Default
Air Handling/Exhaust Fan/Duct/Discharge Air Flow
Air Handling/Exhaust Fan/Duct/Discharge Air Humidity
Air Handling/Exhaust Fan/Duct/Discharge Air Pressure
Air Handling/Exhaust Fan/Duct/Discharge Air Pressure Setpoint
Air Handling/Exhaust Fan/Duct/Discharge Air Temperature
Air Handling/Exhaust Fan/Duct/Discharge Air Temperature Setpoint
Air Handling/Exhaust Fan/Duct/Duct CO2 Sensor
Air Handling/Exhaust Fan/Duct/Duct Flow Control
Air Handling/Exhaust Fan/Duct/Duct Humidity Sensor
Air Handling/Exhaust Fan/Duct/Duct Pressure Sensor
Air Handling/Exhaust Fan/Duct/Duct Temperature Sensor
Air Handling/Exhaust Fan/Duct/Flow Sensor
Air Handling/Exhaust Fan/Duct/Mixed Air Temperature
Air Handling/Exhaust Fan/Duct/Outside Air Flow
Air Handling/Exhaust Fan/Duct/Outside Air Humidity
Air Handling/Exhaust Fan/Duct/Outside Air Temperature
Air Handling/Exhaust Fan/Duct/Return Air CO2
Air Handling/Exhaust Fan/Duct/Return Air DeHumidify Setpoint
Air Handling/Exhaust Fan/Duct/Return Air Humidify Setpoint
Air Handling/Exhaust Fan/Duct/Return Air Humidity
Air Handling/Exhaust Fan/Duct/Return Air Pressure
Air Handling/Exhaust Fan/Duct/Return Air Pressure Setpoint
Air Handling/Exhaust Fan/Duct/Return Air Temperature
Air Handling/Exhaust Fan/Duct/Return CO2 Setpoint
Air Handling/Exhaust Fan/Fan
Air Handling/Exhaust Fan/Fan/Boolean Default
Air Handling/Exhaust Fan/Fan/Boolean Fan Command
Air Handling/Exhaust Fan/Fan/Discharge Air Fan Frequency
Air Handling/Exhaust Fan/Fan/Discharge Air Fan Speed
Air Handling/Exhaust Fan/Fan/Discharge Air Fan Status
Air Handling/Exhaust Fan/Fan/Discharge Fan Command
Air Handling/Exhaust Fan/Fan/Duct Flow Control
Air Handling/Exhaust Fan/Fan/Elapsed Active Time
Air Handling/Exhaust Fan/Fan/Electrical Current
Air Handling/Exhaust Fan/Fan/Electrical Energy Consumption
Air Handling/Exhaust Fan/Fan/Fan Speed Setpoint
Air Handling/Exhaust Fan/Fan/Flow Sensor
Air Handling/Exhaust Fan/Fan/Multi Speed Fan Command
Air Handling/Exhaust Fan/Fan/Multi Speed Fan State
Air Handling/Exhaust Fan/Fan/Return Air Fan Command
Air Handling/Exhaust Fan/Fan/Return Air Fan Frequency
Air Handling/Exhaust Fan/Fan/Return Air Fan Speed
Air Handling/Exhaust Fan/Fan/Return Air Fan Status
Air Handling/Exhaust Fan/Fan/Running State
Air Handling/Exhaust Fan/Fan/Variable Fan Command
Air Handling/Exhaust Fan/Fan/Variable Fan State
Air Handling/Exhaust Fan/Filter
Air Handling/Exhaust Fan/Filter/Filter Alarm
Air Handling/Exhaust Fan/Filter/Filter Pressure Delta
Air Handling/Exhaust Fan/Information
Air Handling/Exhaust Fan/Parking Exhaust
Air Handling/Exhaust Fan/Parking Exhaust/Boolean Default
Air Handling/Exhaust Fan/Parking Exhaust/Damper
Air Handling/Exhaust Fan/Parking Exhaust/Damper/Boolean Default
Air Handling/Exhaust Fan/Parking Exhaust/Damper/Damper Analog Command
Air Handling/Exhaust Fan/Parking Exhaust/Damper/Damper Boolean Command
Air Handling/Exhaust Fan/Parking Exhaust/Damper/Damper Position
Air Handling/Exhaust Fan/Parking Exhaust/Damper/Damper State
Air Handling/Exhaust Fan/Parking Exhaust/Damper/Mixed Air Damper Analog Command
Air Handling/Exhaust Fan/Parking Exhaust/Damper/Outside Air Damper Analog Command
Air Handling/Exhaust Fan/Parking Exhaust/Damper/Outside Air Damper Boolean Command
Air Handling/Exhaust Fan/Parking Exhaust/Damper/Return Air Damper Analog Command
Air Handling/Exhaust Fan/Parking Exhaust/Duct
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Boolean Default
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Discharge Air Flow
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Discharge Air Humidity
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Discharge Air Pressure
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Discharge Air Pressure Setpoint
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Discharge Air Temperature
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Discharge Air Temperature Setpoint
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Duct CO2 Sensor
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Duct Flow Control
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Duct Humidity Sensor
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Duct Pressure Sensor
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Duct Temperature Sensor
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Flow Sensor
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Mixed Air Temperature
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Outside Air Flow
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Outside Air Humidity
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Outside Air Temperature
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Return Air CO2
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Return Air DeHumidify Setpoint
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Return Air Humidify Setpoint
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Return Air Humidity
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Return Air Pressure
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Return Air Pressure Setpoint
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Return Air Temperature
Air Handling/Exhaust Fan/Parking Exhaust/Duct/Return CO2 Setpoint
Air Handling/Exhaust Fan/Parking Exhaust/Fan
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Boolean Default
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Boolean Fan Command
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Discharge Air Fan Frequency
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Discharge Air Fan Speed
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Discharge Air Fan Status
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Discharge Fan Command
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Duct Flow Control
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Elapsed Active Time
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Electrical Current
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Electrical Energy Consumption
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Fan Speed Setpoint
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Flow Sensor
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Multi Speed Fan Command
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Multi Speed Fan State
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Return Air Fan Command
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Return Air Fan Frequency
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Return Air Fan Speed
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Return Air Fan Status
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Running State
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Variable Fan Command
Air Handling/Exhaust Fan/Parking Exhaust/Fan/Variable Fan State
Air Handling/Exhaust Fan/Parking Exhaust/Filter
Air Handling/Exhaust Fan/Parking Exhaust/Filter/Filter Alarm
Air Handling/Exhaust Fan/Parking Exhaust/Filter/Filter Pressure Delta
Air Handling/Exhaust Fan/Parking Exhaust/Information
Air Handling/Exhaust Fan/VEX
Air Handling/Exhaust Fan/VEX/Fan
Air Handling/Exhaust Fan/VEX/Fan/Boolean Default
Air Handling/Exhaust Fan/VEX/Fan/Boolean Fan Command
Air Handling/Exhaust Fan/VEX/Fan/Discharge Air Fan Frequency
Air Handling/Exhaust Fan/VEX/Fan/Discharge Air Fan Speed
Air Handling/Exhaust Fan/VEX/Fan/Discharge Air Fan Status
Air Handling/Exhaust Fan/VEX/Fan/Discharge Fan Command
Air Handling/Exhaust Fan/VEX/Fan/Duct Flow Control
Air Handling/Exhaust Fan/VEX/Fan/Elapsed Active Time
Air Handling/Exhaust Fan/VEX/Fan/Electrical Current
Air Handling/Exhaust Fan/VEX/Fan/Electrical Energy Consumption
Air Handling/Exhaust Fan/VEX/Fan/Fan Speed Setpoint
Air Handling/Exhaust Fan/VEX/Fan/Flow Sensor
Air Handling/Exhaust Fan/VEX/Fan/Multi Speed Fan Command
Air Handling/Exhaust Fan/VEX/Fan/Multi Speed Fan State
Air Handling/Exhaust Fan/VEX/Fan/Return Air Fan Command
Air Handling/Exhaust Fan/VEX/Fan/Return Air Fan Frequency
Air Handling/Exhaust Fan/VEX/Fan/Return Air Fan Speed
Air Handling/Exhaust Fan/VEX/Fan/Return Air Fan Status
Air Handling/Exhaust Fan/VEX/Fan/Running State
Air Handling/Exhaust Fan/VEX/Fan/Variable Fan Command
Air Handling/Exhaust Fan/VEX/Fan/Variable Fan State
Air Handling/Terminal Unit
Air Handling/Terminal Unit/Air Temperature Effective Setpoint
Air Handling/Terminal Unit/Cooling Ceiling
Air Handling/Terminal Unit/Cooling Ceiling/Air Humidity Setpoint
Air Handling/Terminal Unit/Cooling Ceiling/Air Temperature Effective Setpoint
Air Handling/Terminal Unit/Cooling Ceiling/Air Temperature Setpoint
Air Handling/Terminal Unit/Cooling Ceiling/Condensation State Sensor
Air Handling/Terminal Unit/Cooling Ceiling/Cooling Coil
Air Handling/Terminal Unit/Cooling Ceiling/Cooling Coil/Chilled Water Flow
Air Handling/Terminal Unit/Cooling Ceiling/Cooling Coil/Chilled Water Pump Command
Air Handling/Terminal Unit/Cooling Ceiling/Cooling Coil/Chilled Water Pump Status
Air Handling/Terminal Unit/Cooling Ceiling/Cooling Coil/Chilled Water Temp Entering
Air Handling/Terminal Unit/Cooling Ceiling/Cooling Coil/Chilled Water Temp Leaving
Air Handling/Terminal Unit/Cooling Ceiling/Cooling Coil/Chilled Water Valve Command
Air Handling/Terminal Unit/Cooling Ceiling/Cooling Coil/Chilled Water Valve Position
Air Handling/Terminal Unit/Cooling Ceiling/Cooling Coil/Cool Stage Command
Air Handling/Terminal Unit/Cooling Ceiling/Cooling Coil/Cooling Coil Air Leaving Humidity
Air Handling/Terminal Unit/Cooling Ceiling/Cooling Coil/Cooling Coil Air Leaving Temp
Air Handling/Terminal Unit/Cooling Ceiling/Cooling Coil/Pipe Temperature Sensor
Air Handling/Terminal Unit/Cooling Ceiling/Cooling Coil/Pump
Air Handling/Terminal Unit/Cooling Ceiling/Cooling Coil/Pump Boolean Command
Air Handling/Terminal Unit/Cooling Ceiling/Cooling Coil/Pump/Boolean Default
Air Handling/Terminal Unit/Cooling Ceiling/Cooling Coil/Running State
Air Handling/Terminal Unit/Cooling Ceiling/Fan
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Boolean Default
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Boolean Fan Command
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Discharge Air Fan Frequency
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Discharge Air Fan Speed
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Discharge Air Fan Status
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Discharge Fan Command
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Duct Flow Control
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Elapsed Active Time
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Electrical Current
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Electrical Energy Consumption
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Fan Speed Setpoint
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Flow Sensor
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Multi Speed Fan Command
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Multi Speed Fan State
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Return Air Fan Command
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Return Air Fan Frequency
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Return Air Fan Speed
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Return Air Fan Status
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Running State
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Variable Fan Command
Air Handling/Terminal Unit/Cooling Ceiling/Fan/Variable Fan State
Air Handling/Terminal Unit/Cooling Ceiling/HVAC Mode Command
Air Handling/Terminal Unit/Cooling Ceiling/Heating Coil
Air Handling/Terminal Unit/Cooling Ceiling/Heating Coil/Heat Stage Command
Air Handling/Terminal Unit/Cooling Ceiling/Heating Coil/Heating Coil Air Leaving Temp
Air Handling/Terminal Unit/Cooling Ceiling/Heating Coil/Hot Water Circulation Pump Command
Air Handling/Terminal Unit/Cooling Ceiling/Heating Coil/Hot Water Circulation Pump Status
Air Handling/Terminal Unit/Cooling Ceiling/Heating Coil/Hot Water Flow
Air Handling/Terminal Unit/Cooling Ceiling/Heating Coil/Hot Water Temp Entering
Air Handling/Terminal Unit/Cooling Ceiling/Heating Coil/Hot Water Temp Leaving
Air Handling/Terminal Unit/Cooling Ceiling/Heating Coil/Hot Water Valve Command
Air Handling/Terminal Unit/Cooling Ceiling/Heating Coil/Hot Water Valve Status
Air Handling/Terminal Unit/Cooling Ceiling/Heating Coil/Pipe Temperature Sensor
Air Handling/Terminal Unit/Cooling Ceiling/Heating Coil/Pump
Air Handling/Terminal Unit/Cooling Ceiling/Heating Coil/Pump Boolean Command
Air Handling/Terminal Unit/Cooling Ceiling/Heating Coil/Pump/Boolean Default
Air Handling/Terminal Unit/Cooling Ceiling/Heating Coil/Running State
Air Handling/Terminal Unit/Cooling Ceiling/Occupancy Sensor
Air Handling/Terminal Unit/Cooling Ceiling/Occupied Mode
Air Handling/Terminal Unit/Cooling Ceiling/Zone CO2
Air Handling/Terminal Unit/Cooling Ceiling/Zone Humidity
Air Handling/Terminal Unit/Damper
Air Handling/Terminal Unit/Damper/Boolean Default
Air Handling/Terminal Unit/Damper/Damper Analog Command
Air Handling/Terminal Unit/Damper/Damper Boolean Command
Air Handling/Terminal Unit/Damper/Damper Position
Air Handling/Terminal Unit/Damper/Damper State
Air Handling/Terminal Unit/Damper/Mixed Air Damper Analog Command
Air Handling/Terminal Unit/Damper/Outside Air Damper Analog Command
Air Handling/Terminal Unit/Damper/Outside Air Damper Boolean Command
Air Handling/Terminal Unit/Damper/Return Air Damper Analog Command
Air Handling/Terminal Unit/FCU
Air Handling/Terminal Unit/FCU/Air Humidity Setpoint
Air Handling/Terminal Unit/FCU/Air Temperature Effective Setpoint
Air Handling/Terminal Unit/FCU/Air Temperature Setpoint
Air Handling/Terminal Unit/FCU/Alarm Synthesis
Air Handling/Terminal Unit/FCU/Changeover Coil
Air Handling/Terminal Unit/FCU/Condensation State Sensor
Air Handling/Terminal Unit/FCU/Cooling Coil
Air Handling/Terminal Unit/FCU/Cooling Coil/Chilled Water Flow
Air Handling/Terminal Unit/FCU/Cooling Coil/Chilled Water Pump Command
Air Handling/Terminal Unit/FCU/Cooling Coil/Chilled Water Pump Status
Air Handling/Terminal Unit/FCU/Cooling Coil/Chilled Water Temp Entering
Air Handling/Terminal Unit/FCU/Cooling Coil/Chilled Water Temp Leaving
Air Handling/Terminal Unit/FCU/Cooling Coil/Chilled Water Valve Command
Air Handling/Terminal Unit/FCU/Cooling Coil/Chilled Water Valve Position
Air Handling/Terminal Unit/FCU/Cooling Coil/Cool Stage Command
Air Handling/Terminal Unit/FCU/Cooling Coil/Cooling Coil Air Leaving Humidity
Air Handling/Terminal Unit/FCU/Cooling Coil/Cooling Coil Air Leaving Temp
Air Handling/Terminal Unit/FCU/Cooling Coil/Pipe Temperature Sensor
Air Handling/Terminal Unit/FCU/Cooling Coil/Pump
Air Handling/Terminal Unit/FCU/Cooling Coil/Pump Boolean Command
Air Handling/Terminal Unit/FCU/Cooling Coil/Pump/Boolean Default
Air Handling/Terminal Unit/FCU/Cooling Coil/Running State
Air Handling/Terminal Unit/FCU/Damper
Air Handling/Terminal Unit/FCU/Damper/Boolean Default
Air Handling/Terminal Unit/FCU/Damper/Damper Analog Command
Air Handling/Terminal Unit/FCU/Damper/Damper Boolean Command
Air Handling/Terminal Unit/FCU/Damper/Damper Position
Air Handling/Terminal Unit/FCU/Damper/Damper State
Air Handling/Terminal Unit/FCU/Damper/Mixed Air Damper Analog Command
Air Handling/Terminal Unit/FCU/Damper/Outside Air Damper Analog Command
Air Handling/Terminal Unit/FCU/Damper/Outside Air Damper Boolean Command
Air Handling/Terminal Unit/FCU/Damper/Return Air Damper Analog Command
Air Handling/Terminal Unit/FCU/Discharge Air Temperature
Air Handling/Terminal Unit/FCU/Fan
Air Handling/Terminal Unit/FCU/Fan/Boolean Default
Air Handling/Terminal Unit/FCU/Fan/Boolean Fan Command
Air Handling/Terminal Unit/FCU/Fan/Discharge Air Fan Frequency
Air Handling/Terminal Unit/FCU/Fan/Discharge Air Fan Speed
Air Handling/Terminal Unit/FCU/Fan/Discharge Air Fan Status
Air Handling/Terminal Unit/FCU/Fan/Discharge Fan Command
Air Handling/Terminal Unit/FCU/Fan/Duct Flow Control
Air Handling/Terminal Unit/FCU/Fan/Elapsed Active Time
Air Handling/Terminal Unit/FCU/Fan/Electrical Current
Air Handling/Terminal Unit/FCU/Fan/Electrical Energy Consumption
Air Handling/Terminal Unit/FCU/Fan/Fan Speed Setpoint
Air Handling/Terminal Unit/FCU/Fan/Flow Sensor
Air Handling/Terminal Unit/FCU/Fan/Multi Speed Fan Command
Air Handling/Terminal Unit/FCU/Fan/Multi Speed Fan State
Air Handling/Terminal Unit/FCU/Fan/Return Air Fan Command
Air Handling/Terminal Unit/FCU/Fan/Return Air Fan Frequency
Air Handling/Terminal Unit/FCU/Fan/Return Air Fan Speed
Air Handling/Terminal Unit/FCU/Fan/Return Air Fan Status
Air Handling/Terminal Unit/FCU/Fan/Running State
Air Handling/Terminal Unit/FCU/Fan/Variable Fan Command
Air Handling/Terminal Unit/FCU/Fan/Variable Fan State
Air Handling/Terminal Unit/FCU/HVAC Mode Command
Air Handling/Terminal Unit/FCU/Heating Coil
Air Handling/Terminal Unit/FCU/Heating Coil/Heat Stage Command
Air Handling/Terminal Unit/FCU/Heating Coil/Heating Coil Air Leaving Temp
Air Handling/Terminal Unit/FCU/Heating Coil/Hot Water Circulation Pump Command
Air Handling/Terminal Unit/FCU/Heating Coil/Hot Water Circulation Pump Status
Air Handling/Terminal Unit/FCU/Heating Coil/Hot Water Flow
Air Handling/Terminal Unit/FCU/Heating Coil/Hot Water Temp Entering
Air Handling/Terminal Unit/FCU/Heating Coil/Hot Water Temp Leaving
Air Handling/Terminal Unit/FCU/Heating Coil/Hot Water Valve Command
Air Handling/Terminal Unit/FCU/Heating Coil/Hot Water Valve Status
Air Handling/Terminal Unit/FCU/Heating Coil/Pipe Temperature Sensor
Air Handling/Terminal Unit/FCU/Heating Coil/Pump
Air Handling/Terminal Unit/FCU/Heating Coil/Pump Boolean Command
Air Handling/Terminal Unit/FCU/Heating Coil/Pump/Boolean Default
Air Handling/Terminal Unit/FCU/Heating Coil/Running State
Air Handling/Terminal Unit/FCU/Occupancy Sensor
Air Handling/Terminal Unit/FCU/Occupied Cooling Setpoint
Air Handling/Terminal Unit/FCU/Occupied Heating Setpoint
Air Handling/Terminal Unit/FCU/Occupied Mode
Air Handling/Terminal Unit/FCU/Pre Heating Coil
Air Handling/Terminal Unit/FCU/Pre Heating Coil/Hot Water Circulation Pump Command
Air Handling/Terminal Unit/FCU/Pre Heating Coil/Hot Water Circulation Pump Status
Air Handling/Terminal Unit/FCU/Pre Heating Coil/Hot Water Flow
Air Handling/Terminal Unit/FCU/Pre Heating Coil/Hot Water Temp Entering
Air Handling/Terminal Unit/FCU/Pre Heating Coil/Hot Water Temp Leaving
Air Handling/Terminal Unit/FCU/Pre Heating Coil/Pipe Temperature Sensor
Air Handling/Terminal Unit/FCU/Pre Heating Coil/PreHeat Coil Air Leaving Temp
Air Handling/Terminal Unit/FCU/Pre Heating Coil/Preheat Valve Command
Air Handling/Terminal Unit/FCU/Pre Heating Coil/Preheat Valve Status
Air Handling/Terminal Unit/FCU/Pre Heating Coil/Pump
Air Handling/Terminal Unit/FCU/Pre Heating Coil/Pump Boolean Command
Air Handling/Terminal Unit/FCU/Pre Heating Coil/Pump/Boolean Default
Air Handling/Terminal Unit/FCU/Pre Heating Coil/Running State
Air Handling/Terminal Unit/FCU/Unoccupied Cooling Setpoint
Air Handling/Terminal Unit/FCU/Unoccupied Heating Setpoint
Air Handling/Terminal Unit/FCU/Zone CO2
Air Handling/Terminal Unit/FCU/Zone Humidity
Air Handling/Terminal Unit/FCU/Zone Temperature
Air Handling/Terminal Unit/FCU/Zone Temperature Setpoint Effective
Air Handling/Terminal Unit/Fan
Air Handling/Terminal Unit/Fan/Boolean Default
Air Handling/Terminal Unit/Fan/Boolean Fan Command
Air Handling/Terminal Unit/Fan/Discharge Air Fan Frequency
Air Handling/Terminal Unit/Fan/Discharge Air Fan Speed
Air Handling/Terminal Unit/Fan/Discharge Air Fan Status
Air Handling/Terminal Unit/Fan/Discharge Fan Command
Air Handling/Terminal Unit/Fan/Duct Flow Control
Air Handling/Terminal Unit/Fan/Elapsed Active Time
Air Handling/Terminal Unit/Fan/Electrical Current
Air Handling/Terminal Unit/Fan/Electrical Energy Consumption
Air Handling/Terminal Unit/Fan/Fan Speed Setpoint
Air Handling/Terminal Unit/Fan/Flow Sensor
Air Handling/Terminal Unit/Fan/Multi Speed Fan Command
Air Handling/Terminal Unit/Fan/Multi Speed Fan State
Air Handling/Terminal Unit/Fan/Return Air Fan Command
Air Handling/Terminal Unit/Fan/Return Air Fan Frequency
Air Handling/Terminal Unit/Fan/Return Air Fan Speed
Air Handling/Terminal Unit/Fan/Return Air Fan Status
Air Handling/Terminal Unit/Fan/Running State
Air Handling/Terminal Unit/Fan/Variable Fan Command
Air Handling/Terminal Unit/Fan/Variable Fan State
Air Handling/Terminal Unit/HVAC Mode Command
Air Handling/Terminal Unit/Heated Air Curtains
Air Handling/Terminal Unit/Heated Air Curtains/Fan
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Boolean Default
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Boolean Fan Command
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Discharge Air Fan Frequency
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Discharge Air Fan Speed
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Discharge Air Fan Status
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Discharge Fan Command
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Duct Flow Control
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Elapsed Active Time
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Electrical Current
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Electrical Energy Consumption
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Fan Speed Setpoint
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Flow Sensor
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Multi Speed Fan Command
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Multi Speed Fan State
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Return Air Fan Command
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Return Air Fan Frequency
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Return Air Fan Speed
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Return Air Fan Status
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Running State
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Variable Fan Command
Air Handling/Terminal Unit/Heated Air Curtains/Fan/Variable Fan State
Air Handling/Terminal Unit/Heating Coil
Air Handling/Terminal Unit/Heating Coil/Heat Stage Command
Air Handling/Terminal Unit/Heating Coil/Heating Coil Air Leaving Temp
Air Handling/Terminal Unit/Heating Coil/Hot Water Circulation Pump Command
Air Handling/Terminal Unit/Heating Coil/Hot Water Circulation Pump Status
Air Handling/Terminal Unit/Heating Coil/Hot Water Flow
Air Handling/Terminal Unit/Heating Coil/Hot Water Temp Entering
Air Handling/Terminal Unit/Heating Coil/Hot Water Temp Leaving
Air Handling/Terminal Unit/Heating Coil/Hot Water Valve Command
Air Handling/Terminal Unit/Heating Coil/Hot Water Valve Status
Air Handling/Terminal Unit/Heating Coil/Pipe Temperature Sensor
Air Handling/Terminal Unit/Heating Coil/Pump
Air Handling/Terminal Unit/Heating Coil/Pump Boolean Command
Air Handling/Terminal Unit/Heating Coil/Pump/Boolean Default
Air Handling/Terminal Unit/Heating Coil/Running State
Air Handling/Terminal Unit/Occupancy Sensor
Air Handling/Terminal Unit/Occupied Mode
Air Handling/Terminal Unit/Split
Air Handling/Terminal Unit/VAV
Air Handling/Terminal Unit/VAV/Air Temperature Effective Setpoint
Air Handling/Terminal Unit/VAV/Cooling Max Flow
Air Handling/Terminal Unit/VAV/Cooling Min Flow
Air Handling/Terminal Unit/VAV/Damper
Air Handling/Terminal Unit/VAV/Damper/Boolean Default
Air Handling/Terminal Unit/VAV/Damper/Damper Analog Command
Air Handling/Terminal Unit/VAV/Damper/Damper Boolean Command
Air Handling/Terminal Unit/VAV/Damper/Damper Position
Air Handling/Terminal Unit/VAV/Damper/Damper State
Air Handling/Terminal Unit/VAV/Damper/Mixed Air Damper Analog Command
Air Handling/Terminal Unit/VAV/Damper/Outside Air Damper Analog Command
Air Handling/Terminal Unit/VAV/Damper/Outside Air Damper Boolean Command
Air Handling/Terminal Unit/VAV/Damper/Return Air Damper Analog Command
Air Handling/Terminal Unit/VAV/Discharge Air Flow
Air Handling/Terminal Unit/VAV/Discharge Air Flow Setpoint Effective
Air Handling/Terminal Unit/VAV/Discharge Air Temperature
Air Handling/Terminal Unit/VAV/Flow Sensor
Air Handling/Terminal Unit/VAV/HVAC Mode Command
Air Handling/Terminal Unit/VAV/Heating Coil
Air Handling/Terminal Unit/VAV/Heating Coil/Heat Stage Command
Air Handling/Terminal Unit/VAV/Heating Coil/Heating Coil Air Leaving Temp
Air Handling/Terminal Unit/VAV/Heating Coil/Hot Water Circulation Pump Command
Air Handling/Terminal Unit/VAV/Heating Coil/Hot Water Circulation Pump Status
Air Handling/Terminal Unit/VAV/Heating Coil/Hot Water Flow
Air Handling/Terminal Unit/VAV/Heating Coil/Hot Water Temp Entering
Air Handling/Terminal Unit/VAV/Heating Coil/Hot Water Temp Leaving
Air Handling/Terminal Unit/VAV/Heating Coil/Hot Water Valve Command
Air Handling/Terminal Unit/VAV/Heating Coil/Hot Water Valve Status
Air Handling/Terminal Unit/VAV/Heating Coil/Pipe Temperature Sensor
Air Handling/Terminal Unit/VAV/Heating Coil/Pump
Air Handling/Terminal Unit/VAV/Heating Coil/Pump Boolean Command
Air Handling/Terminal Unit/VAV/Heating Coil/Pump/Boolean Default
Air Handling/Terminal Unit/VAV/Heating Coil/Running State
Air Handling/Terminal Unit/VAV/Heating Max Flow
Air Handling/Terminal Unit/VAV/Heating Min Flow
Air Handling/Terminal Unit/VAV/Occupancy Sensor
Air Handling/Terminal Unit/VAV/Occupied Cooling Setpoint
Air Handling/Terminal Unit/VAV/Occupied Heating Setpoint
Air Handling/Terminal Unit/VAV/Occupied Mode
Air Handling/Terminal Unit/VAV/Reheat Valve Command
Air Handling/Terminal Unit/VAV/Unoccupied Cooling Setpoint
Air Handling/Terminal Unit/VAV/Unoccupied Heating Setpoint
Air Handling/Terminal Unit/VAV/Zone CO2
Air Handling/Terminal Unit/VAV/Zone CO2 Setpoint
Air Handling/Terminal Unit/VAV/Zone Humidity
Air Handling/Terminal Unit/VAV/Zone Humidity Setpoint
Air Handling/Terminal Unit/VAV/Zone Temperature
Air Handling/Terminal Unit/VAV/Zone Temperature Setpoint Effective
Air/Compressed air
Air/Makeup Air
Alimentation CPCU
Boolean
Boolean Alarm
Boolean/Alarm
Boolean/Authorization
Boolean/Confirmation
Boolean/Default
Boolean/Eco Mode
Boolean/Enabling
Boolean/Flow State
Boolean/Lighting
Boolean/Occupancy
Boolean/Open Closed
Boolean/Running
Close Control Unit
Command
Command/Analog Command
Command/Binary Command
Command/Enum Command
Concentration
Concentration/CO Concentration
Concentration/CO2 Concentration
Cooling Type
Cooling Type/Chilled Water Cool
Cooling Type/Dx Cool
Cooling Type/No Cool
Current
Damper Type
Damper Type/2-Way
Damper Type/3-Way
Damper Type/Bypass
Damper Type/Fire
Damper Type/Isolation
Damper Type/Mixed
Default Type
Default Type/Belt
Default Type/Clogged
Default Type/Device Failure
Default Type/Fire
Default Type/Flow
Default Type/Freeze
Default Type/General
Default Type/Hygrostat
Default Type/Overheat
Default Type/Overpressure
Default Type/Smoke
Default Type/Thermostat
Default Type/Threshold
Default Type/Underpressure
Default Type/Water Deficiency
Direct Expansion Cooling Coil
Discharge
Duct Differential Pressure Sensor
Duct Type
Duct Type/Cold Deck
Duct Type/Hot Deck
Duct Type/Neutral Deck
Electricity
Energy
Entering
Epingle
Exhaust
Fan Type
Fan Type/Multi Speed
Fan Type/Simple
Fan Type/Variable Speed
Flow
Frequency
Fresh Air
Furnace
Gas
Heating Type
Heating Type/Electric Heat
Heating Type/Gas Heat
Heating Type/Hot Water Heat
Heating Type/No Heat
Heating Type/Steam Heat
Hot Water Tank
Humidity
Hydrogen
Information Type
Information Type/Cleaning in Progress
Information Type/Maintenance In Progress
Information Type/Master*/*Slave
Information Type/Switch State
Leaving
Liquid nitrogen
Luminosity
Measure
Meter
Metering
Metering/Meter
Metering/Meter/Electricity Meter
Metering/Meter/Electricity Meter/Active Power Total Sensor
Metering/Meter/Electricity Meter/Electrical Energy Consumption
Metering/Meter/Electricity Meter/Power Sensor
Metering/Meter/Gas Meter
Mixed
Movement
Outside
Outside
Outside/Outside Humidity Sensor
Outside/Outside Temperature Sensor
Ouvrants
Ouvrants/Sky dome
Overheat Air Thermostat
Oxygen
Percentage
Photovoltaic Panel
Pipe Differential Pressure Sensor
Pipe Flow Sensor
Pipe Oxygen Pressure Sensor
Pipe Water Presence Sensor
Position
Power
Power Type
Power Type/Active
Power Type/Apparent
Power Type/Reactive
Preheat
Pressure
Pressure Control
Pressure Control/Filter Monitoring
Pressure Control/Flow control
Pressure Control/Negative Pressure
Pressure Control/Positive Pressure
Pressure/Differential Pressure
Production
Production/Compressed air production
Production/Cooling Production
Production/Cooling Production/Chiller plant
Production/Cooling Production/Compressor
Production/Cooling Production/DRY
Production/Cooling Production/DRY/Fan
Production/Cooling Production/DRY/Fan/Boolean Default
Production/Cooling Production/DRY/Fan/Boolean Fan Command
Production/Cooling Production/DRY/Fan/Discharge Air Fan Frequency
Production/Cooling Production/DRY/Fan/Discharge Air Fan Speed
Production/Cooling Production/DRY/Fan/Discharge Air Fan Status
Production/Cooling Production/DRY/Fan/Discharge Fan Command
Production/Cooling Production/DRY/Fan/Duct Flow Control
Production/Cooling Production/DRY/Fan/Elapsed Active Time
Production/Cooling Production/DRY/Fan/Electrical Current
Production/Cooling Production/DRY/Fan/Electrical Energy Consumption
Production/Cooling Production/DRY/Fan/Fan Speed Setpoint
Production/Cooling Production/DRY/Fan/Flow Sensor
Production/Cooling Production/DRY/Fan/Multi Speed Fan Command
Production/Cooling Production/DRY/Fan/Multi Speed Fan State
Production/Cooling Production/DRY/Fan/Return Air Fan Command
Production/Cooling Production/DRY/Fan/Return Air Fan Frequency
Production/Cooling Production/DRY/Fan/Return Air Fan Speed
Production/Cooling Production/DRY/Fan/Return Air Fan Status
Production/Cooling Production/DRY/Fan/Running State
Production/Cooling Production/DRY/Fan/Variable Fan Command
Production/Cooling Production/DRY/Fan/Variable Fan State
Production/Heat Cool Production
Production/Heat Production
Production/Heat Production/Hot Water production
Production/Heat Production/Hot Water production/Préparateur ECS
Production/Heat Pump
Production/Heat Pump/Elapsed Active Time
Pump Group
Pump Group/Pump
Pump Group/Pump/Boolean Default
Pump Type
Pump Type/Single Pump
Quality Air Sensor
Return
Rooftop
Rooftop/Damper
Rooftop/Damper/Boolean Default
Rooftop/Damper/Damper Analog Command
Rooftop/Damper/Damper Boolean Command
Rooftop/Damper/Damper Position
Rooftop/Damper/Damper State
Rooftop/Damper/Mixed Air Damper Analog Command
Rooftop/Damper/Outside Air Damper Analog Command
Rooftop/Damper/Outside Air Damper Boolean Command
Rooftop/Damper/Return Air Damper Analog Command
Rooftop/Fan
Rooftop/Fan/Boolean Default
Rooftop/Fan/Boolean Fan Command
Rooftop/Fan/Discharge Air Fan Frequency
Rooftop/Fan/Discharge Air Fan Speed
Rooftop/Fan/Discharge Air Fan Status
Rooftop/Fan/Discharge Fan Command
Rooftop/Fan/Duct Flow Control
Rooftop/Fan/Elapsed Active Time
Rooftop/Fan/Electrical Current
Rooftop/Fan/Electrical Energy Consumption
Rooftop/Fan/Fan Speed Setpoint
Rooftop/Fan/Flow Sensor
Rooftop/Fan/Multi Speed Fan Command
Rooftop/Fan/Multi Speed Fan State
Rooftop/Fan/Return Air Fan Command
Rooftop/Fan/Return Air Fan Frequency
Rooftop/Fan/Return Air Fan Speed
Rooftop/Fan/Return Air Fan Status
Rooftop/Fan/Running State
Rooftop/Fan/Variable Fan Command
Rooftop/Fan/Variable Fan State
Setpoint
Setpoint Type
Setpoint Type/Antifreeze
Setpoint Type/Comfort
Setpoint Type/Cooling
Setpoint Type/Heating
Setpoint Type/Occupied Cooling
Setpoint Type/Occupied Heating
Setpoint Type/Offset
Setpoint Type/Optimized
Setpoint Type/Reduced
Setpoint Type/Standby Cooling
Setpoint Type/Standby Heating
Setpoint Type/Stop
Setpoint Type/Unoccupied Cooling
Setpoint Type/Unoccupied Heating
Setting Type
Setting Type/Master*/*Slave
Setting Type/VAV Configuration
Settings
Speed
State
State/Analog Feedback
State/Binary State
State/Multi State
Temperature
Time
VRV
VRV/Fan
VRV/Fan/Boolean Default
VRV/Fan/Boolean Fan Command
VRV/Fan/Discharge Air Fan Frequency
VRV/Fan/Discharge Air Fan Speed
VRV/Fan/Discharge Air Fan Status
VRV/Fan/Discharge Fan Command
VRV/Fan/Duct Flow Control
VRV/Fan/Elapsed Active Time
VRV/Fan/Electrical Current
VRV/Fan/Electrical Energy Consumption
VRV/Fan/Fan Speed Setpoint
VRV/Fan/Flow Sensor
VRV/Fan/Multi Speed Fan Command
VRV/Fan/Multi Speed Fan State
VRV/Fan/Return Air Fan Command
VRV/Fan/Return Air Fan Frequency
VRV/Fan/Return Air Fan Speed
VRV/Fan/Return Air Fan Status
VRV/Fan/Running State
VRV/Fan/Variable Fan Command
VRV/Fan/Variable Fan State
Vacuum
Valve Type
Valve Type/2-Way
Valve Type/3-Way
Valve Type/4-Way
Valve Type/Blow Off
Valve Type/Bypass
Valve Type/Cleanning
Valve Type/Filling
Valve Type/Isolation
Volt
Water
Water Softening
Water Softening/Boolean Default
Water Softening/Water Softening State
Water distribution
Water distribution/Cooling Distribution
Water distribution/Cooling Distribution/Circuit régulé
Water distribution/Cooling Distribution/Constant circuit
Water distribution/Distribution ChangeOver
Water distribution/Distribution ChangeOver/Circuit régulé
Water distribution/Distribution ChangeOver/Constant circuit
Water distribution/Heat Distribution
Water distribution/Heat Distribution/Boiler
Water distribution/Heat Distribution/Boiler/Boolean Default
Water distribution/Heat Distribution/Boiler/Burner
Water distribution/Heat Distribution/Boiler/Fuel Boiler
Water distribution/Heat Distribution/Boiler/Fuel Boiler/Boolean Default
Water distribution/Heat Distribution/Boiler/Fuel Boiler/Burner
Water distribution/Heat Distribution/Boiler/Gas Boiler
Water distribution/Heat Distribution/Boiler/Gas Boiler/Boolean Default
Water distribution/Heat Distribution/Boiler/Gas Boiler/Burner
Water distribution/Heat Distribution/Boiler/Wood Boiler
Water distribution/Heat Distribution/Boiler/Wood Boiler/Boolean Default
Water distribution/Heat Distribution/Circuit régulé
Water distribution/Heat Distribution/Constant circuit
Water/Blowdown Water
Water/Chilled Water
Water/Domestic Cold Water
Water/Domestic Hot Water
Water/Hot Water
Water/Makeup Water
Water/Steam
Zone
Zone
Zone/Boolean Default
Zone/CO2 Detection System
Zone/CO2 Detection System/Boolean Default
Zone/Occupied Cooling Setpoint
Zone/Occupied Heating Setpoint
Zone/Unoccupied Cooling Setpoint
Zone/Unoccupied Heating Setpoint
Zone/Zone Air Quality Sensor
Zone/Zone CO Sensor
Zone/Zone CO2
Zone/Zone CO2 Setpoint
Zone/Zone Differential Pressure Sensor
Zone/Zone Humidity
Zone/Zone Humidity Setpoint
Zone/Zone Hygrostat Alarm
Zone/Zone Luminosity Sensor
Zone/Zone Pressure
Zone/Zone Pressure Setpoint
Zone/Zone Smoke Detector
Zone/Zone Temperature
Zone/Zone Temperature Setpoint Effective

## ~Variables
General |  | Alarms |  | Histories |  | Conversions |  | Facets
Artifact | Value | Artifact | Value | Artifact | Value | Artifact | Value | Artifact | Value
$ModbusAsyncNetwork | modbusAsync:ModbusAsyncNetwork | $OutOfRange | excel:OutOfRangeAlarmExt | $NumericInterval | history:NumericIntervalHistoryExt | $NO | Default | $BooleanFacet | trueText=s:true;falseText=s:false
$ModbusAsyncDevice | modbusAsync:ModbusAsyncDevice | $StringChangeOfValue | excel:StringChangeOfValueAlarmExt | $NumericCov | history:NumericCovHistoryExt | $NF | ReversePolarity | $EnumFacet | range={}
$Station | slot: | $BooleanChangeOfState | excel:BooleanChangeOfStateAlarmExt | $BooleanInterval | history:BooleanIntervalHistoryExt | $Linear | Linear(1,1) | $NumericFacet | min=-inf;max=+inf;precision=i:1;units=null
$Drivers | slot:/Drivers | $BooleanCommandFailure | excel:BooleanCommandFailureAlarmExt | $BooleanCov | history:BooleanCovHistoryExt
$Num | control:NumericPoint | $EnumChangeOfState | excel:EnumChangeOfStateAlarmExt | $EnumInterval | history:EnumIntervalHistoryExt
$Bool | control:BooleanPoint | $EnumCommandFailure | excel:EnumCommandFailureAlarmExt | $EnumCov | history:EnumCovHistoryExt
$Enum | control:EnumPoint | $Status | excel:StatusAlarmExt | $StringInterval | history:StringIntervalHistoryExt
$String | control:StringPoint | $Loop | excel:LoopAlarmExt | $StringCov | history:StringCovHistoryExt
$BooleanSchedule | schedule:BooleanSchedule | $ElapsedActiveTime | excel:ElapsedActiveTimeAlarmExt
|  | $ChangeOfStateCount | excel:ChangeOfStateCountAlarmExt